	
	Unit Data
	
	
	Motor Data
	
	

	
	Make
	Carrier
	
	Make/Frame
	GE/56Y
	

	
	Model Number
	50HJ008V531
	
	H.P./RPM
	NA/1725
	

	
	Serial Number
	1709G50526
	
	Volts/Phase/Hertz
	208/3/60
	

	
	Make Sheave
	Fennis
	
	Full Load Amps/S.F.
	7.5/8.4
	

	
	Sheave Diam/Bore
	7”/1”
	
	Make Sheave
	Power Drive
	

	
	No. Belts/Size
	1/A-49
	
	Sheave Diam/Bore
	5”/7/8”
	

	
	
	
	
	Sheave CL Distance
	3/8”
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	


                                                                                                                                   Package Rooftop Unit

                                                                                                                                                   Test Report

Project:       Southern Park of Commerce                                                                  System:       RTU-1

Location:     Building “B”, Bay 6, West Palm Beach, Florida

	
	Evaporator Data
	Design
	Actual
	
	Condensor Data
	Compr #1
	Compr #2
	

	
	Total CFM
	3000
	3025
	
	Refrigerant/Lbs./Ozs.
	22/7/9.6
	22/8/1.6
	

	
	Total E.S.P.
	NA
	-
	
	Compr. Manufacturer
	Copeland
	Copeland
	

	
	Discharge S.P.
	NA
	-
	
	Compr. Model Number
	ZR42K3TF5230
	ZR42K3TF5230
	

	
	Suction S.P.
	NA
	-
	
	Compr. Serial Number
	09DC6570L
	09DC6552L
	

	
	Outside Air CFM
	200
	192
	
	
	
	
	

	
	Outside Air DB/WB
	NA
	84.8/73.1
	
	
	
	
	

	
	Return Air CFM
	2800
	2833
	
	
	
	
	

	
	Return Air DB/WB
	NA
	74.3/62.6
	
	Condensor Fan HP
	¼
	¼
	

	
	Entering Air DB/WB
	NA
	74.7/63.2
	
	No. of Fans/Fan RPM
	2/1100
	2/1100
	

	
	Leaving Air DB/WB
	NA
	58.5/58.9
	
	Cond FanVolt/Phase/Hz
	208/1/60
	208/1/60
	

	
	Fan RPM
	NA
	1725
	
	Condensor Fan Amps
	1.4
	1.4
	

	
	Motor VoltageT1T2T3
	208
	210
	
	Compr. Volts T1 T2 T3
	210 209 210
	209 209 210
	

	
	Motor Amperage T1

                            T2

                            T3
	7.5

7.5

7.5
	7.2

7.3

7.2
	
	Compr. Amps T1

                        T2

                        T3
	11.9

12.1

11.8
	12.1

12.0

11.9
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	


Remarks:

Test Date: 12-01-09                                             Readings By: Martinez                                              Page 1 of 5

